ENGINEERING CONTROL PHILOSOPHY

Water-Tank PCS and SIS Control System

Split-range tank level control, duty/standby discharge pumps and independent 2oo3 high-high/low-low protection

| Document | Revision | Issue date | Status |
| --- | --- | --- | --- |
| WT-PCS-SIS-CP-001 | A | 02 Aug 2026 | Simulation Complete - Hardware Validation Pending |

Prepared by Simon Kamua

PLC/SIS Technician | ICSS Commissioning, Troubleshooting and Process Safety

# Document status and safety boundary

This document records an independently developed educational control-system design. It uses simulated values and sanitized tags and contains no employer-owned drawings, operating data, screenshots, controller backups or configuration files.

| Evidence label | Meaning |
| --- | --- |
| Design documented | Process purpose, architecture, I/O, alarms, sequences and protection responses are defined. |
| Desktop tested | Reference-model checks and the interactive browser simulation have been exercised. |
| Not hardware validated | No compiled Omron project, field I/O, FAT, SAT, live process connection or SIL verification is claimed. |

Safety notice: The ESP32-S3 is not a certified safety PLC. The demonstrator must not be used for an operational safety instrumented function.

# 1. Purpose and scope

A reservoir feeds TK-101 through fail-close LCV-101. Two VFD pumps, P-101A and P-101B, discharge the tank in duty/standby service. The Omron PCS maintains level using an inventory-reduction controller whose split-range outputs progressively close the inlet valve and increase discharge-pump speed as level rises. A separate ESP32-S3 educational demonstrator receives LT-201A/B/C and applies independent 2oo3 votes: high-high closes and inhibits the inlet; low-low trips and inhibits both discharge pumps.

## 1.1 Objectives

Maintain TK-101 close to the illustrative 55% operating setpoint under changing inlet and downstream conditions.

Coordinate fail-close LCV-101 and the selected discharge pump through an explicit split-range characteristic.

Select duty and standby pumps in the PCS and perform a status-verified bumpless changeover.

Detect start failure, unexpected stop, VFD/motor faults, speed deviation, no-flow operation and loss of both pumps.

Demonstrate separate 2oo3 high-high inlet shutdown and low-low pump shutdown functions with latching and manual reset.

## 1.2 Design assumptions

LCV-101 is installed on the reservoir-to-tank inlet and fails closed on loss of its protective permit.

P-101A/B are parallel discharge pumps downstream of TK-101, with a 30% illustrative minimum stable VFD speed.

LT-101 is the normal PCS measurement and uses detected upscale burnout handling.

LT-201A/B/C are separate protection measurements with individual quality and disagreement diagnostics.

Protection outputs override PCS commands through independent de-energize-to-trip interfaces.

## 1.3 Explicit exclusions

No SIL claim, SIL verification, PFDavg calculation, certified diagnostics or proof-test coverage is provided.

No live process connection, hydraulic sizing, NPSH study, valve Cv calculation, pump-curve validation or network design is included.

Illustrative setpoints, tuning, delays and actuator limits are not suitable for direct plant application.

The ESP32-S3 is not a certified safety PLC and must not be used for operational protection.

# 2. Process and control architecture

The normal PCS and the educational protection layer are separated by measurement and function. LT-101 supports continuous PCS control. LT-201A/B/C support separate high-high and low-low votes. Protective outputs override ordinary PCS commands.

Figure 1 - Conceptual process and control architecture

## 2.1 Functional separation

| Layer | Normal responsibility | Protective override |
| --- | --- | --- |
| Omron PCS | Level control, split range, pump selection, permissives, changeover, alarms and operator interface. | Must accept HH inlet-trip and LL pump-trip status; cannot defeat them. |
| ESP32-S3 demonstrator | No normal control responsibility. | 2oo3 HH closes inlet; 2oo3 LL trips pumps; separate latches and reset permissives. |
| Final elements | LCV-101 and selected VFD pump follow PCS demands when permits are healthy. | De-energized protection permits force the defined action. |

# 3. Normal control philosophy

## 3.1 Controller action

LIC-101 produces an inventory-reduction demand. The demand rises when tank level rises above the 55% setpoint and falls when tank level falls below setpoint. This naming makes the direction explicit: a larger output asks the system to reduce stored inventory.

## 3.2 Illustrative split range

| Demand band | LCV-101 response | Active pump response | Control intent |
| --- | --- | --- | --- |
| 0-35% | 100% open | 30% minimum speed | Recover low inventory while preserving minimum discharge. |
| 35-65% | 100% to 40% open | 30% to 50% speed | Overlapping coordinated response around normal operation. |
| 65-100% | 40% to 0% open | 50% to 100% speed | Reduce high inventory by restricting inlet and increasing outflow. |

The overlap, limits, gains and ramps are simulation assumptions. Final values require pump curves, valve characteristics, process dynamics and commissioning tests.

## 3.3 PCS level-transmitter failure

LT-101 uses detected upscale burnout handling. A bad or out-of-range signal raises an alarm, forces the inlet closed and blocks new automatic pump starting. A running pump is held at a configured tracked bias pending operator intervention. Independent protection remains available through LT-201A/B/C.

# 4. Operating modes and sequence

| Mode/state | Control intent |
| --- | --- |
| Stopped | Pumps stopped; inlet closed unless an authorized fill mode is active; monitoring and protection remain active. |
| Manual | Authorized output proving with equipment interlocks and independent protection overrides retained. |
| Automatic | LIC-101 regulates tank inventory while the PCS manages the selected duty pump and standby availability. |
| Changeover | The incoming pump starts and ramps to tracked demand before the outgoing pump ramps down and stops. |
| High-high trip | The protection layer closes and inhibits LCV-101; an eligible discharge pump remains available. |
| Low-low trip | The protection layer trips and inhibits both discharge pumps until level recovery and manual reset. |
| Degraded | A bad or disagreeing channel is annunciated; reset is blocked until voting health is restored. |

## 4.1 Sequence of operations

| Step | Phase | Required behavior |
| --- | --- | --- |
| 1 | Pre-start validation | Confirm LT-101 valid, no low-low trip, selected pump available, downstream path healthy and protection status acceptable. |
| 2 | Start duty pump | Start the selected discharge pump at 30%; prove run feedback and speed response before the timeout. |
| 3 | Enable automatic control | Track current outputs, then release LIC-101 to automatic inventory control. |
| 4 | Split-range response | As level rises, progressively close LCV-101 and increase discharge-pump speed; reverse the response as level falls. |
| 5 | Controlled changeover | Start standby, prove run feedback, ramp to tracked demand, unload the old duty pump, stop it and transfer duty. |
| 6 | Pump-fault transfer | Remove the failed pump, latch the initiating fault and transfer to the healthy standby when available. |
| 7 | High-high protection | On 2oo3 at 90%, close and inhibit LCV-101; do not trip a healthy discharge pump solely for high level. |
| 8 | Low-low protection | On 2oo3 at 15%, trip and inhibit both discharge pumps to prevent dry running. |
| 9 | Reset and recovery | Require HH below 85% or LL above 20%, healthy channels and a deliberate manual reset. |

# 5. Duty/standby pump management

## 5.1 Availability permissives

Local emergency stop healthy.

VFD ready and communications healthy.

No motor overload or active VFD fault.

Remote operating mode selected.

Tank level above the low-low reset threshold.

No active maintenance inhibit.

Low-low protection trip reset.

Downstream flow path available.

## 5.2 Bumpless changeover

| Step | Action | Confirmation |
| --- | --- | --- |
| 1 | Validate the selected standby pump. | All availability permissives true. |
| 2 | Issue start command at minimum stable speed. | Run feedback before timeout. |
| 3 | Ramp incoming pump toward tracked demand. | Speed feedback within 2% of demand. |
| 4 | Ramp outgoing pump toward zero. | Incoming pump remains stable. |
| 5 | Stop outgoing pump and transfer duty designation. | Stopped feedback and new duty status confirmed. |

## 5.3 Fault response

| Fault | Detection | Automatic response |
| --- | --- | --- |
| Pump command with no run feedback | 5 s | Fail start; mark unavailable; start healthy standby |
| Run feedback lost with command active | 0.5 s | Remove command; transfer to healthy standby |
| VFD fault or motor overload | 0 s | Stop affected pump; latch fault; transfer duty |
| Speed deviation > 10% | 5 s | Alarm; hold changeover; transfer if performance inadequate |
| Low discharge flow while running | 5 s | Stop affected pump; attempt standby transfer |
| Both pumps unavailable | 0 s | High-priority alarm; close inlet as level rises |

# 6. Independent protection philosophy

LT-201A, LT-201B and LT-201C are treated as independent educational input channels. A protective action requires two valid channels to cross the applicable threshold. A single abnormal channel does not trip, but disagreement or invalid quality is annunciated and reset is blocked until channel health returns.

| Initiating event | Vote | Automatic action | Reset condition |
| --- | --- | --- | --- |
| High-high level | 2oo3 >= 90% | Close and inhibit LCV-101. Keep an eligible discharge pump available. | All valid channels < 85% and manual reset. |
| Low-low level | 2oo3 <= 15% | Trip and inhibit P-101A and P-101B. | All valid channels > 20% and manual reset. |
| Channel disagreement | Spread > 5% for delay | Degraded alarm; identify channel; no automatic trip from disagreement alone. | Agreement restored and acknowledged. |
| Invalid channel | Quality diagnostic | Degraded alarm; invalid channel does not count as safe; block reset. | All channels valid and voting state verified. |
| Protection power loss | De-energize-to-trip | Close inlet and remove pump permit. | Power and diagnostics healthy, then manual reset. |

## 6.1 Real-SIS boundary

A real SIS requires an approved Safety Requirements Specification, hazard analysis, independence review, SIL verification, certified hardware, proof-test procedures and controlled management of bypasses and overrides. Those lifecycle activities are outside this portfolio demonstrator.

# 7. Setpoints and alarms

| Parameter | Value | Units | Purpose |
| --- | --- | --- | --- |
| Normal level setpoint | 55 | % | PCS target |
| High-level alarm | 80 | % | Operator warning |
| High-high trip | 90 | % | 2oo3 inlet shutdown |
| High-high reset | 85 | % | Reset hysteresis |
| Low-level alarm | 25 | % | Operator warning |
| Low-low trip | 15 | % | 2oo3 pump shutdown |
| Low-low reset | 20 | % | Reset hysteresis |
| Channel disagreement | 5 | % span | Degraded alarm |

## 7.1 Alarm and interlock register

| ID | Initiating condition | Priority | Delay | Response | Reset |
| --- | --- | --- | --- | --- | --- |
| A-001 | LT-101 >= 80% | High | 2 s | Warn operator; controller increases inventory reduction | Auto clear |
| A-002 | LT-101 <= 25% | High | 2 s | Warn operator; controller reduces discharge demand | Auto clear |
| A-003 | LT-101 bad or out of range | High | 1 s | Close inlet; block new auto start; hold running pump at safe tracked bias | Manual confirm |
| A-004 | Any two LT-201 channels >= 90% | Trip | 0.5 s | Close and inhibit LCV-101; keep eligible discharge pump available | Manual below 85% |
| A-005 | Any two LT-201 channels <= 15% | Trip | 0.5 s | Trip and inhibit P-101A/B | Manual above 20% |
| A-006 | Protection-channel spread > 5% | Medium | 5 s | Identify disagreeing channel; degraded alarm | Healthy + acknowledge |
| A-007 | Any protection channel invalid | High | 1 s | Degraded alarm; block protective reset | All channels valid |
| A-008 | Pump command with no run feedback | High | 5 s | Fail start; mark unavailable; start healthy standby | Manual / auto transfer |
| A-009 | Run feedback lost with command active | High | 0.5 s | Remove command; transfer to healthy standby | Manual |
| A-010 | VFD fault or motor overload | High | 0 s | Stop affected pump; latch fault; transfer duty | Manual |
| A-011 | Speed deviation > 10% | Medium | 5 s | Alarm; hold changeover; transfer if performance inadequate | Auto clear / manual |
| A-012 | Low discharge flow while running | High | 5 s | Stop affected pump; attempt standby transfer | Manual |
| A-013 | Both pumps unavailable | High | 0 s | High-priority alarm; close inlet as level rises | Availability restored |
| A-014 | LCV demand/position mismatch | High | 5 s | Alarm; inhibit unsafe restart | Manual |

# 8. Functional I/O

The following signals are conceptual. Actual addresses, marshalling, electrical protection, network mapping and channel diagnostics remain hardware-project deliverables.

| Tag | I/O | Signal | Description | Range/state | Fail state | Owner |
| --- | --- | --- | --- | --- | --- | --- |
| LT-101 | AI | 4-20 mA | PCS tank level | 0-100% | Upscale / bad quality | PCS |
| LT-201A | AI | 4-20 mA | Protection level channel A | 0-100% | Invalid channel | Protection demo |
| LT-201B | AI | 4-20 mA | Protection level channel B | 0-100% | Invalid channel | Protection demo |
| LT-201C | AI | 4-20 mA | Protection level channel C | 0-100% | Invalid channel | Protection demo |
| FIT-101 | AI | 4-20 mA | Common pump-discharge flow | 0-150 m3/h | Bad quality | PCS |
| PIT-101 | AI | 4-20 mA | Common pump-discharge pressure | 0-10 bar | Bad quality | PCS |
| LCV-101.POS | AI | 4-20 mA | Inlet-valve position feedback | 0-100% | Bad quality | PCS |
| LCV-101.CMD | AO | 4-20 mA | Inlet-valve position demand | 0-100% | 0% / closed | PCS + HH override |
| P-101A.SPD | AO/Net | 0-100% | Pump A speed reference | 0-100% | 0% | PCS |
| P-101B.SPD | AO/Net | 0-100% | Pump B speed reference | 0-100% | 0% | PCS |
| P-101A.RUN | DI | 24 Vdc | Pump A run feedback | Run/Stop | Stopped | PCS |
| P-101B.RUN | DI | 24 Vdc | Pump B run feedback | Run/Stop | Stopped | PCS |
| P-101A.READY | DI/Net | Boolean | Pump A VFD ready | Ready/Not ready | Not ready | PCS |
| P-101B.READY | DI/Net | Boolean | Pump B VFD ready | Ready/Not ready | Not ready | PCS |
| P-101A.FLT | DI/Net | Boolean | Pump A VFD fault | Healthy/Fault | Fault | PCS |
| P-101B.FLT | DI/Net | Boolean | Pump B VFD fault | Healthy/Fault | Fault | PCS |
| P-101A.REM | DI | 24 Vdc | Pump A remote mode | Remote/Local | Local | PCS |
| P-101B.REM | DI | 24 Vdc | Pump B remote mode | Remote/Local | Local | PCS |
| P-101A.START | DO | 24 Vdc | Pump A start/stop command | Run/Stop | Stop | PCS + LL override |
| P-101B.START | DO | 24 Vdc | Pump B start/stop command | Run/Stop | Stop | PCS + LL override |
| SIS.RESET | DI | Momentary | Protection manual reset | Pressed/Released | Released | Protection demo |
| SIS.INLET_PERMIT | DO | De-energize | Permit LCV-101 to open | Permit/Trip | Trip / close | Protection demo |
| SIS.PUMP_PERMIT | DO | De-energize | Permit P-101A/B to run | Permit/Trip | Trip / stop | Protection demo |
| SIS.STATUS | DI/Net | Boolean word | Trip/degraded status to PCS | Status bits | Unhealthy | Protection demo to PCS |

# 9. Logic architecture

| Logic section | Responsibility |
| --- | --- |
| Input conditioning | Scaling, quality, range checks, debounce and conservative bad-signal substitution. |
| Modes and permissives | Auto/manual, start/stop, selected duty, downstream readiness and trip status. |
| Level control | Inventory-reduction controller, tracking, limits and split-range mapping. |
| Pump manager | Availability, run proving, speed ramping, duty transfer and fault response. |
| Protection interface | Independent HH inlet override, LL pump override, status and reset interlocks. |
| Protection demonstrator | Three channel diagnostics, 2oo3 HH/LL voting, separate latches and safe outputs. |
| Alarms and events | Priorities, first-out, changeover events and functional-test evidence. |

## 9.1 Omron ladder-logic section schedule

| Rung | Section | Logic intent |
| --- | --- | --- |
| 000-019 | Input handling | Scale LT/FIT/PIT; validate quality; debounce status |
| 020-039 | Modes | Auto/manual, start/stop and duty selection |
| 040-069 | Permissives | Pump readiness, downstream path and protection status |
| 070-109 | Control | LIC inventory demand and split-range outputs |
| 110-169 | Pump manager | Run proving, ramping and bumpless changeover |
| 170-219 | Faults | Start fail, unexpected stop, speed mismatch, no flow and VFD trips |
| 220-249 | Protection interface | HH inlet override, LL pump override and status |
| 250-289 | Alarms | Priorities, first-out and reset |
| 290-319 | HMI | Commands, status, diagnostics and events |

# 10. Verification plan and desktop results

Desktop results demonstrate consistency between the design rules, deterministic checks and the public HTML simulation. They do not represent hardware FAT or SAT.

| Test | Scenario | Precondition | Expected result | Result | Evidence |
| --- | --- | --- | --- | --- | --- |
| WT-001 | Normal automatic start | Level 55%; duty A ready | A starts at minimum speed; tracked auto control enabled | PASS | Reference model + HTML |
| WT-002 | High-level disturbance | Auto stable | LCV closes progressively; discharge speed increases | PASS | Reference model + HTML |
| WT-003 | Low-level disturbance | Auto stable above LL | LCV opens; discharge speed reduces toward minimum | PASS | Reference model + HTML |
| WT-004 | Duty changeover A to B | Both pumps ready | B reaches tracked demand before A stops | PASS | HTML simulation |
| WT-005 | Duty-pump failure | A duty; B ready | A is removed and B assumes duty | PASS | HTML fault injection |
| WT-006 | PCS LT burnout | Auto running | Inlet closes; new auto starts blocked; protection remains available | PASS | Reference model |
| WT-007 | One LT-201 channel high | Other channels normal | No HH trip; disagreement/degraded indication | PASS | Reference model + HTML |
| WT-008 | Two channels high-high | Protection healthy | Inlet trip latches; discharge pump remains available | PASS | Reference model + HTML |
| WT-009 | One LT-201 channel low | Other channels normal | No LL trip | PASS | Reference model |
| WT-010 | Two channels low-low | Protection healthy | Both pumps trip and restart is inhibited | PASS | Reference model + HTML |
| WT-011 | Reset with active cause | HH or LL remains active | Reset rejected | PASS | Design inspection + HTML |
| WT-012 | Channel invalid | Trip latched | Degraded alarm; reset blocked | PASS | Code inspection |

## 10.1 Hardware FAT still required

Compile the selected Omron project with no errors or unresolved I/O.

Verify every analog scale, discrete state, fail direction and command/feedback pair.

Test threshold boundaries, time delays, latches, reset permissives and controller restart behavior.

Measure pump-transfer timing and confirm no unacceptable level or pressure disturbance.

Record witness, defect, retest, backup and software-checksum evidence.

# 11. Engineering decisions and next development

| Decision | Engineering rationale |
| --- | --- |
| Inventory-reduction demand | A rising controller output means more inventory removal: close the inlet and increase discharge capacity. |
| Correct protective split | High-high removes inflow but preserves healthy outflow; low-low removes pump outflow to prevent dry running. |
| Separate transmitters | LT-101 serves normal control while LT-201A/B/C provide an independent educational voting layer. |
| Manual reset with hysteresis | Separate reset thresholds prevent chatter and automatic restart at the trip boundary. |
| Bumpless pump transfer | Proving and loading the incoming pump before unloading the outgoing pump reduces hydraulic disturbance. |

## 11.1 Known limitations

The simplified model omits pump curves, NPSH, valve stiction, line packing and pressure transients.

PID tuning, split-range overlap and ramps are illustrative and require validated process data.

The ST listing is a design reference, not a compiled Omron hardware project.

The ESP32-S3 lacks certified diagnostics, systematic capability and independence evidence.

## 11.2 Recommended development

Implement the selected Omron PID block with tracking, anti-windup and validated tuning.

Add run-hour balancing, maintenance counters and equipment plausibility diagnostics.

Build a low-voltage rig and execute witnessed FAT-style tests.

Use certified hardware and complete an SRS and SIL verification before any genuine safety application.

End of controlled portfolio document.